CORRinSITE Model 7800

2.1 SPRINKLER SPECIALTY PIPE FITTINGS

* + - * 1. In-Line Corrosion Monitor for Wet and Dry Pipe Fire Sprinkler Systems:

Manufacturers: Subject to compliance with requirements, available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

AGF Manufacturing Inc.; CORRinSITE™ Model 7800.

<**Insert manufacturer's name**>.

Standards:

NFPA 13 and NFPA 25.

Specifications:

Service Pressure: 300 PSI.

Operating Temp.: -40° to 200° F.

Material: Mild Carbon Steel.

Wear Dimension: 0.040 inch.

Sizes: [**2**] [**2-1/2**] [**3**] [**4**] [**6**] [**8**] inches.

Schedule [**10**] [**40**].

For Black and Galvanized Pipe.

Model 7800 is offered in a Mechanical Tee versions

Finishes:

Powder-coat.

Color: Red.

Hot-dip galvanized.